# Alpha2( Small Wet Rotor Circulator

# Part I – GENERAL

## 1.1	WORK INCLUDED

A.  Contractor shall furnish and install Grundfos Alpha2 variable speed wet rotor in–line circulator pumps in accordance with manufacturer’s recommendations and plans.

## 1.2	REFERENCE STANDARDS

The work in this section is subject to the requirements of applicable portions of the following standards:

- Hydraulic Institute

- ANSI – American National Standards Institute

- ASTM – American Society for Testing and Materials

- IEEE – Institute of Electrical and Electronics Engineers

- NEMA – National Electrical Manufacturers Association

- NEC – National Electrical Code

- ISO – International Standards Organization

- UL – Underwriters Laboratories, Inc.

- CSA –Canadian Standards Association

- ETL – ETL Listed Mark by Intertek Testing Services

## INSTALLATION REFERENCES

The wet runner pump manufacturer shall have minimum 10 years of experience in the country of the installation.

# Part 2 – PRODUCTS

## 2.1	VARIABLE SPEED WET ROTOR CIRCULATOR PUMPS

- Pump shall be of the in-line wet rotor design.  Oil lubricated pumps and shaft coupled pumps shall not be accepted.

- The pump shall be a standard product of a single pump manufacturer.  The pump, motor, and variable speed drive shall be an integral product designed and built by the same manufacturer.

- The enclosure shall be marked “IP42”.

- The pump shall be certified and listed by a Nationally Recognized Test Laboratory (NRTL) for U.S. and Canada to comply with:

  - UL778

  - UL 60730-1A

  - CAN/CSA No. 108

- The pump shall be labeled on the nameplate as having an Energy Efficiency Index (EEI) of no greater than 0.24.

## 2.1.1	Ratings

- Maximum Pressure: 				145 PSIG

- Minimum Media Temperature:			36 °F

- Maximum Media Temperature			230 °F

- Maximum Continuous Media Temperature: 	203 °F

- Maximum Sound Pressure Level:			43dB(A)

- Voltage:						[1x115V +/-10%]

- Maximum Energy Efficiency Index:		0.24

## 2.1.2	Pump Construction

- Pump housing:			Cast Iron: EN-JGL-250 with Cataphorese surface treatment

Stainless Steel:	304 Stainless

- Impellers:			Composite PES 30% GF

- Rotor Can:			304 Stainless Steel

- Rotor Cladding:			316 Stainless Steel

- Shaft:				Ceramic

- Thrust Bearing:			Carbon Graphie

- Gaskets:			EPDM

- Bearing Plate:			304 Stainless Steel

- Control Box:			Polycarbonate

## Motor

- Motor shall be 4-pole permanent-magnet (PM motor) and tested with the pump as one unit by the same manufacturer.  Conventional asynchronous squirrel-cage motors shall not be acceptable.

- Each motor shall be of the integrated Variable Speed Drive design consisting of a motor and a Variable Frequency Drive (VFD) built and tested as one unit by the same manufacturer.

- The motor shall be cooled by the pumped fluid

- The power electronics shall be cooled to the ambient air.

- The Motor shall be self-ventilating.

- Minimum insulation class for the motor shall be Class F.

## Operating Modes

The pump shall have the following control mode and operating modes:

- AutoAdapt – Controls the pump performance automatically within the defined

performance range based on the sensed demand.

- Constant Pressure – A manual set, constant head is maintained, irrespective of flow up to the maximum speed of the pump.

- Constant Speed – The pump runs as an uncontrolled pump by the means of a set of pump curves.  The pump curve is adjustable between 3 curve sets from the control panel.

## Performance

The pump shall have the following performance characteristics:

- Model Alpha2 15-55 shall be rated to consume a maximum of 45W.

## Interface and Communication

- The pump shall have an integrated operator interface consisting of:

    - Push button for navigation of operating modes

    - LEDs to signal pump operating mode for quick indication

## INSTALLATION

The pump shaft shall be installed horizontally per manufacturer’s recommendations. The terminal box shall be located as per manufacturer’s recommendations.  The system shall be vented out from a higher location form the pump. The required inlet pressure by the pump shall be available at the pump inlet.

## 2.3   TESTING

A.	The pumps shall be factory performance and hydrostatic tested as a complete unit prior to shipment. The testing shall be done in accordance with ISO 9906 Annex A. No test certificate is required.

## 2.4	WARRANTY

- The warranty period shall be a non-prorated period of 12 months from date of installation, not to exceed 18 months from date of manufacture. Warranty shall cover pump, motor and terminal box as a complete unit.